## Slide 1: CalFIRE A2L 2022
JUne 2020

## Slide 3: New HVAC Installation with New Line-set

## Slide 4: New Install with Existing Line-set –Exposed Piping
** If there are joints in existing line-set in walls , those joints would have been inspected prior to cover up in original installation.
IDENTICAL
**
**
IDENTICAL
IDENTICAL
IDENTICAL
IDENTICAL
A2L more stringent

## Slide 5: New Install with Existing Line-set –Hidden Piping
California Building Code has required visible inspection of piping upon installation as far back as could be confirmed.
Verify piping integrity (whether existing or new): pressure test, vacuum check, and leak check

## Slide 6: Research

## Slide 7: Completed Research on Flammable Refrigerants*
Testing
  AHRTI-9007: Benchmarking Risk by Whole Room Scale Leaks and Ignitions Testing
  AHRTI-9013: A2L Consequence Study
  AHRTI-9012/Oak Ridge National Laboratory (ORNL): Real-world Leak Assessments of Alternative Flammable Refrigerants-Phase I
  AHRTI-9008: Investigation of Hot surface Ignition Temperature (HSIT) for A2L Refrigerants
  AHRI-8017: Investigation of Energy Produced by Potential Ignition Sources in Residential Application
  NFPA: Evaluation of the Fire Hazard of ASHRAE Class A3 Refrigerants in Commercial Refrigeration Applications
  Carrier: Electric Heater Testing
  Carrier: Turbulent deﬂagrations of mildly ﬂammable refrigerant-air mixtures
Modeling
  ORNL: Investigate the Proper Basis for Setting Charge Limits of A2L, A2, and A3 for Various Types of Products
  Servicing
  ASHRAE-1807:Guidelines for Flammable Refrigerant Handling, Transporting, Storing and Equipment Servicing, Installation and Dismantling
  ASHRAE-1808: Servicing and Installing Equipment using Flammable Refrigerants: Assessment of Field-made Mechanical Joints
  AHAM Safe Servicing of Household Appliances with Flammable Refrigerants: Recommended Practices
  NFPA: Flammable refrigerants firefighter training: Hazard assessment and demonstrative testing
Detection
  AHRTI-9009: Leak Detection of A2L Refrigerants in HVACR Equipment
*This is not a comprehensive list (Japan, Europe and Manufacturers have done extensive studies)

## Slide 8: Research on Flammable Refrigerants*
Completed - Risk Assessment
  AHRI-8004: Risk Assessment of Residential Heat Pump Systems Using 2L Flammable Refrigerants
  AHRI-8009: Risk Assessment of Refrigeration Systems Using A2L Flammable Refrigerants
  AHRI-8016: Risk Assessment of Rooftop Units Using A2L Refrigerants
Ongoing projects in US
  AHRTI-9014: Assess Refrigerant Detector Characteristics for Use in HVACR Equipment
  AHRTI-9015: Assessment of Mitigation Effectiveness for Air-Conditioning and Refrigeration Equipment
  AHRI 8023: Risk Assessment of Transport Refrigeration Systems Using Flammable Refrigerants
  Oak Ridge National Laboratory (ORNL): Real-world Leak Assessments of Alternative Flammable-Phase II
  NIST: Modeling tools for low-GWP Refrigerant Blends Flammability
  ASHRAE-1806: Flammable Refrigerants Post-Ignition Simulation and Risk Assessment Update
  ASHRAE-1855: Determination of the Impact of Combustion Byproducts on the Safe Use of Flammable Fluorinated Refrigerants
Research outside US
  Japanese Industry Risk Assessment of Mildly Flammable Refrigerants
  Japanese Industry Risk Assessment for Safe Use of A3 Refrigerants
*This is not a comprehensive list (Japan, Europe and Manufacturers have done extensive studies)

## Slide 9: Research 9007-01
http://www.ahrinet.org/App_Content/ahri/files/RESEARCH/Technical%20Results/AHRI_9007-01_Final_Report.pdf

## Slide 10: AHRTI 9007-01

## Slide 11: Flammable Zones - Initial Research Observations
High (8ft) release: Concentrations below LFL due to mixing
Low release: Concentrations above UFL
Mid-range without barrier: Concentrations below LFL due to mixing
Mid-range with barrier with air circulation: Concentrations below LFL due to mixing
Mid-range with barrier with no circulation: can result in concentrations between LFL and UFL
How safety standards were updated -
Charge size without sensor or ductwork requires use of gravity equation and mixing equations address these learnings

## Slide 12: Release from 8 ft

## Slide 13: Modeling showed that room setup required an obstruction to achieve concentration between LFL and UFL with no circulation/ mitigation

## Slide 14: PTAC Unit in Motel Room
The refrigerant quantity released in the tests corresponds to proposed m1 size charge of (6 m3 × LFL kg/m3), where LFL is the lower flammable limit in kg/m3 from for the refrigerant used.
Nine tests were conducted for this scenario using R-32 and R-452B refrigerants. The ignition sources were tea candles (open flame) placed at floor level or electric arc sources which continually arced once energized at the various locations.
In some of the tests, the candle ignition source failed to either ignite or stay ignited. Refrigerant concentrations measured in the test room did not show values above the LFL and ignition did not occur. One test using R-452B resulted in a low energy ignition near the PTAC power cord plug lasting no more 3 seconds.
There was no secondary ignition of the cheesecloth for either refrigerant in this test. An additional test was added placing the electric arcs directly in front of the PTAC in the refrigerant discharge zone. This test resulted in ignition of the refrigerant.
The PTAC tests were designed to emulate the release of refrigerant from the evaporator into a typical motel room sized 1660 ft³, 47.1 m³ with ignition devices representing those sources that could be expected to occur.

## Slide 15: IEC 60335-2-40 uses 50% LFL to initiate mitigation
IEC uses 50% LFL to initiate mitigation to account for:
  Furniture / obstacles
  Refrigerant density
  Safety factor
  IEC uses 50% LFL while UL uses 25% LFL in standards to initiate mitigation

## Slide 16: How do I know if there is a leak?
The fan will be running and will not turn off.
The unit will not cool or heat.
Bottom line: No cooling or heating + fan running --> There may be a leak
There is a detector inside the equipment that will turn on fan at 25% LFL (or lower) and turn off cooling, heating and electrostatic ignition sources

## Slide 17: Portable Gas or Oxygen detectors
What should the sensor detect? The technology is known and there are many detectors available including intrinsically safe ones.
•Significant leak required to reach LFL
  • LFL (A2Ls) = 118,000 to 144,000 ppm
  •LFL (Butane) = 18,000 ppm
•Sufficient O2- O2 Sensor
•Leak of fluorinated refrigerant- Hand-held leak detectors
  ($200-$300) (10 to 1000 ppm)
•HF- Draeger tubes or HF monitors
  ($200-$600) (10 to 1000 ppm)

## Slide 18: AHRTI 9007-01
Concentrations must be very high to reach LFL

## Slide 19: Sensing Leaks
An odorant (e.g. mercaptan) is added to some highly flammable fluids (e.g. natural gas) to provide a single way to sense the presence of odorless, colorless gases with LFLs at or below 5% and very low ignition energies (natural gas <0.5 milliJoules) that have been involved in severe incidents. Odorant potential usage in AC is still under investigation.
Large volumes of refrigerant must be released in order reach a flammable concentration (greater than 10%), so a high flow rate of refrigerant is needed:
  Loud (sound)
  Refrigerant cloud (sight)
  Cold temperature as refrigerant is released (feel)
Release 25% LFL

## Slide 20: UL/AHRI Demonstration Project
Review proposal through June 1
6 weeks from commencement to draft report
8 weeks to final report
Scenario | Test #1 | Refrigerant | Scenario | Refrigerant
1 | 1 | Baseline | Baseline 60 kW calorimeter measurements | None
 | 2 | A1 #1 | Discharge into open flame from various distances | R-410A
 | 3 | A2L #1 |  | R-32
 | 4 | A2L #2 |  | R-454B
 | 5 | A1 #2 |  | R-466A
2 | 6 | Baseline | Flashover fire A1 room | None
 | 7 | A1 | Flashover fire with refrigerant line break | R-410A
 | 8 | A2L #1 |  | R-32
 | 9 | A2L #2 |  | R-454B
If Needed 3 | 10 | A1 | Flashover fire with fully charged system (no forced break) | R-410A
 | 11 | A2L #1 |  | R-32
 | 12 | A2L #2 |  | R-454B
4 | 13 | Baseline | Combustibles fire in A1 Room | None
 | 14 | A1 | Forced line break during overhaul | R-410A
 | 15 | A2L #1 |  | R-32
 | 16 | A2L #2 |  | R-454B
5 | 17 | Baseline | Kitchen gas fire in Room | None
 | 18 | A1 | Kitchen cooktop gas fire with refrigerant line break | R-410A
 | 19 | A2L #1 |  | R-32
 | 20 | A2L #2 |  | R-454B

## Slide 21: AHRI Safe Refrigerant Transition Task Force
AHRI has formed a Safe Transition Task Force which has 7 working groups that are open to interested participants
Goals are to evaluate end-to-end supply chain to enable the safe commercialization of low GWP refrigerants in a timely manner and support the effort to reverse the global warming trend.
  Communications
  Safety Training
  Codes and Standards
  Transportation/Storage/Packaging/Handling
  Bulk Storage and Manufacturing Facilities
  Installation/Operation/Maintenance
  Recovery/Reclaim/Destruction
Establish structure to ensure continuous improvement
  Incident investigation
  Continuous maintenance standards
  Training upgrades
Leverage learnings around the world
  Widespread use of A2L refrigerants already in global HVAC&R industry in European Union, Japan, India and Australia and auto industry (including US and Canada)
http://www.ahrinet.org/SafeRefrigerant
Contact one of the following people if interested in the Safe Refrigerant Transition Task Force
Helen Water-Terrinoni HWalter-Terrinoni@ahrinet.org
Christophe Bresee CBresee@ahrinet.org

## Slide 22: END CHARTS FROM MAY MEETING

## Slide 23: CalFIRE A2L 2022
June 11 2020

## Slide 24: EPA Significant New Alternatives Policy (SNAP) Program Rule 23
Signed by EPA Administrator Wheeler May 29th
45-day public comment commences when proposed rule is published in the Federal Register (likely later this month).
  Residential and light commercial air conditioning and heat pumps—Proposed listing of R-32, R-452B, R-454A, R-454B, R-454C, and R-457A as acceptable, subject to use conditions, for use in residential and light commercial air conditioning and heat pumps end-use for new equipment;
  Total flooding: Proposed removal of Powdered Aerosol E from the list of substitutes acceptable subject to use conditions
https://www.epa.gov/sites/production/files/2020-06/documents/pre-publication_snap_listing_rule_23_nprm_5_29_2020_signed_.pdf

## Slide 25: EPA Significant New Alternative Policy (SNAP) Program
SNAP program is required to complete a comparative analysis of alternate refrigerants based on safety, toxicity, environmental properties etc.
  FYI. EPA also lists fire suppressants as acceptable or unacceptable based on the same criteria and has experts in fire suppression alternatives.
  The EPA SNAP program experts have a wide breadth of experience with many of them having been analyzing alternatives for decades. They have expertise in the products using chemicals, toxicity, safety etc.
New refrigerants are only listed as “acceptable” if they can be used without increasing risk compared to the original refrigerant based on this set of criteria.
  Historically, EPA has listed flammable refrigerants as “acceptable only subject to use conditions” which generally include requirements to adhere to a product safety standard such as UL 60335-2-40. There are often charge limits included in EPA’s listing regulations.

## Slide 26: Why 2023 date for AC when SB1383 requires 40% reduction in 2030
SB1013 mandates based on the consumption or use of certain refrigerants 
SB1383 mandates CARB to reduce emissions instead of consumption
  Emission regulations require early action:
2010 -2023 R-410A
Equipment installed
2030 R-410A emissions come from AC equipment installed 2010 – 2023
40% emissions reduction based on lower GWP AC refrigerants installed from 2023-2030
2019: Aerosols can no longer use HFC-134a
2024: Chillers can no longer use R-410A
2021: Self-contained units can no longer use R-404A

## Slide 27: ASHRAE RP-1808: Durability and Leak Rates of Field-made Mechanical Joints
Press fittings, compression fittings and flare fittings.
  2 different fitting sizes between 3/8” and 1-1/8”
  Two different materials (Cu-Cu and Cu-Al).
  100 fittings of each type underwent the evaluation procedure.
  Brazed joints were used as a baseline
Evaluation
  Fitting assembly time,
  Leaks after initial assembly
  Assembly failures for which the fitting required replacement
  Fitting durability through a series of harshness tests
    Pressure-temperature cycling,
    freezing-thawing cycling and
    vibration testing
  Leak rates of different fittings
    positive pressure with R32 vapor
    Vacuum

## Slide 28: Conclusions
Pressure (at not less than the design pressure of the setting of the pressure relief device) and vacuum tests as well as leak check are required in the safety standards
  Leak checks are important after assembly especially for press fittings and compression fittings.
  More experienced technicians assembled fittings faster and there were less leaks from their fittings
  Experience level more important than assembly location and fitting size.
High failure rates of smaller flare fittings at very cold temperatures indicate that they should be avoided in temperatures below freezing
Suggest that care be exercised when using compression and flare (threaded-type) fittings under vibrating application conditions. Fittings may have been damaged during vibration testing.
No significant leaks under vacuum conditions for any of the fittings relative to brazed fittings

## Slide 29: RECALL: 4 lbs would need to be released in a space of less than 212 sq ft to reach LFL
M1 for A2L refrigerants (R-32 & R-454B) is ~ 4 lbs.
  A typical 12K PTAC has less than 2 lbs of R410A (this would go to about 1.7 lbs of R32).
  Old rule of thumb – 80s or 90s construction - 400 ft2 per ton
  New rule of thumb - More recent construction - 600 to 1,000 ft2 per ton
In order to reach the lower flammability limit, 4 lbs of an A2L would need to be released into a room smaller than 6 m3 or 211.9 ft3 or a 5.1 by 5.1 ft room (8 ft ceiling).
Even with the most conservative estimate, a 26.5 square ft. room would only need a much smaller AC unit with a much smaller charge.
Note that mitigation requirements for ignition sources, labeling, and safe application are still required for m1 systems.
AHRTI research examined m1 charged equipment
Bottom Line: A complete release from even a reasonably oversized “m1” unit is unlikely to reach LFL

## Slide 30: m1 A2L Air Conditioning Units have been marketed and sold in US since 2016
https://www.coolingpost.com/world-news/lg-supply-r32-air-conditioners-in-the-us/
https://perfectaire.us/2019/03/22/switching-to-r32-from-r410a-why-manufacturers-are-switching-refrigerants/
Lowe's R32 window units - https://www.lowes.com/pd/LG-550-sq-ft-Window-Air-Conditioner-115-Volt-12000-BTU-ENERGY-STAR/1000925326

## Slide 31: Summary ASHRAE RP-1808
Fitting Type |  | Assembly Failures (/100) | Leaks Found (/100) | Pressure/ Temperature and Freeze/Thaw | Vibration | Observed leak rate g/yr *
Press Fitting | Fastest | 1 |  | 0/100 |  | 1 g/yr
Compression Fitting | Second | 8 | 33 | 5-10% (could be re-tightened) |  | 0.4 g/ yr (near zero leak rate observed for many fittings)
Flare Fittings | Third | 5 | 56 |  | Large flare fittings failed 50% | 0.2 g/ yr (near zero leak rate observed for many fittings)
* Recall 4 lbs charge would need to be released suddenly into less than 212 sq ft to reach LFL.

## Slide 32: Leak Rate Comparison
Annual Leak Rate |  |  | Time to reach LFL in 10' x 10' x 8' room | 
gram | ounce | pound | months | years
1 | 0.0 | 0.0 | 83,134 | 6,928
4 | 0.1 | 0.0 | 20,784 | 1,732
100 | 3.5 | 0.2 | 831 | 69
1000 | 35.3 | 2.2 | 83 | 7

## Slide 33: Is there any difference between flammable fluids?
Different flammable fluids are regulated differently in building codes and other regulations.
  NFPA storage limits are different for acetylene, ammonia, methylene chloride and propane.
  Global Harmonized System differentiates between refrigerant classes.
It takes orders of magnitude higher energy to ignite ASHRAE Class 2L flammable refrigerants versus commonly used hydrocarbons like acetylene, propane and butane
Higher concentrations are needed to reach flammable concentrations compared to A3 refrigerants
Heat of combustion and burning velocity are lower for A2L refrigerants

## Slide 35
It takes 2-6x higher A2L concentration to reach flammable concentrations versus A3 refrigerants
Minimum Ignition Energy: Note the logarithmic scale.

## Slide 36: Research Project 9007-1 (cont)

## Slide 37: Rooftop Unit in Commercial Kitchen
Five tests were conducted for this scenario using R-32 and R-452B refrigerants. Tests represented a refrigerant leak in the evaporator in the air handler.
This location was approximately 9 ft. (2.7m) above the work surfaces. In these tests, the HVAC unit fan was turned on 30s or 60s after the start of refrigerant release as a mitigation technique.
There was accumulation of the leaked refrigerant in the evaporator condensate drain pan and therefore not all the refrigerant entered the test room. This resulted in lower concentrations of refrigerants and no ignition was observed.
In these tests, the candle ignition source was extinguished by the fan-induced flow of the air-refrigerant mixture in the test room.
This test consisted of a roof top unit with duct work connected to the kitchen space below. The kitchen size was 14 x 16 x 8 ft. high (4.3m x 4.9m x 2.4m). The release quantities for R-32 and R-452B were based on a IEC SC 61D Working Group 9 draft version of IEC 60335-2-40 (Annex GG section: GG.10.1).

## Slide 38: Split HVAC unit in utility closet – Internal Leak
The residential A/C application test scenario involved an HVAC unit located in a 24ft 2in x 30ft x 8ft (7.4 x 9.1 x 2.4m) residential arrangement with the air conditioning unit located in a 8 x 4 x 8 ft. (2.4 x 1.2 x 2.4m) closet. In this scenario, three tests were conducted using R-410A, R-32 and R-452B refrigerants. The refrigerant charge used was the same as that used in the A-coil experiments.
The refrigerant was released under natural pressure decay to represent a servicing scenario such as a mistake during joint brazing. In all of these scenarios 30g lubricating oil was mixed with each refrigerant prior to release.
Ignition was not observed with R-410A refrigerant. However, ignition occurred for both R-32 and R-452B refrigerants near the release location which was located inside the closet.
There was no ignition of the refrigerant outside the utility closet for either refrigerant. The candle ignition sources were placed near the point of release.
Once the discharge started, these candles were immediately extinguished by the discharge. Ignition was observed once the electric arc was energized.
The location of the electric arc and the discharge rate combined to limit the ignited volume to the immediate vicinity of the electric arc.
9007-01 Figure 143 – Results residential A/C Res06, R410A
9007-01 Figure 144 – Results for residential A/C Res07, R32
small flame

## Slide 39: Walk-in Cooler
The first two tests were for R455A and R457A at a target charge level with the walk-in door closed. The leak was created at the coil return band.
This would be the worst case scenario when leaked refrigerants were trapped inside the walk-in box, and refrigerant has the tendency to pool when the refrigerant was forced to leave the unit cooler through the condensate drain and drop to the floor. Ignition occurred for both tests.
The tests were repeated with the walk-in door open to see if the refrigerants ignition may be mitigated due to the fact that they can dissipate outside the walk-in box. The position of the test room door, open or closed, appeared to have little impact on ignition results.
Testing results indicated that 13*LFL charge limit without mitigation may have risk under catastrophic refrigerant release.
The published 2-89 3ED is currently set an upper limit: “The refrigerant charge of flammable refrigerant in appliances with an incorporated refrigerant unit or motor-compressor shall not exceed 13 times the LFL of the flammable refrigerant or 1,2 kg in any refrigerating circuit, whichever is smaller.”
The walk-in cooler scenario involved the use of a ceiling mounted commercial refrigeration unit with the refrigerant leak in the evaporator. The refrigerant release quantities were based on 13 m3 × LFL kg m3 (from draft version of IEC 60335-2-89) for R-455A and R-457A.

## Slide 40: Reach-in Cooler The reach-in cooler scenario involved a product display refrigerator having an internal volume of 21 ft³ (0.59 m³), located in a convenience store with dimensions of 30 x 30 x 8-ft. high (9.1m x 9.1m x 2.4m). Tests with release quantities of 300g, 400g, and 500g were performed. The 500 g value is the current limit for class 2 flammable refrigerant in UL 471 edition 10 including revisions through November 2014. Four tests were conducted for this scenario using R-455A and R-457A refrigerants.
The reach-in cooler tests showed that ignition of the refrigerant occurs with a refrigerant release quantity greater than 300g.
The fire spread indicated that walls and corners in proximity of the reach-in cooler facilitate higher concentrations of refrigerants.
In those cases where ignition occurred, the highest temperatures attained were near the floor level.
The 300 gram test showed some flaring of the candles due to the presence of refrigerant, but there was no visible spread of flame into the surrounding air.
Maximum temperatures from the events increased with increasing charge size. Both 400 and 500 gram charge sizes resulted in ignition.
R-455A had approximately 150 ºF lower maximum temperatures than R-457A for the same release mass of 500 grams.

## Slide 41: Hermetic Electrical Pass-Through Terminal Failure
The results from the Hermetic Electrical Terminal failure tests showed that R-452B ignited under these test conditions.
In the R-452B experiment, it was observed that the molded plug remained attached to the terminal which was different from all other experiments where the molded plug was completely ejected.
The experiment with R-410A was repeated because of concern about the seating of the terminal plug on the electrical terminals. In both R-410A tests, there was no ignition.
It was anticipated that R-32 would ignite under these same conditions, but an electrical interference from the electric arc influenced the solenoid valve controlling the refrigerant discharge and caused reduction in the overall rate of R-32 discharge. This slower rate of the R-32 discharge resulted in refrigerant/air mixtures that were not ignitable.
The Hermetic Electrical Terminal failure scenario involved the use of the outdoor section of a residential compressor/condenser unit. Four tests were conducted for this scenario using R-32, R-452B, and R-410A refrigerants. Each test was conducted using a new factory-built compressor charged with refrigerant and lubricating oil. A 1/8 inch hole was drilled in the Hermetic Electrical Terminal plug to represent a terminal failure

## Slide 43: Unlicensed Contractors?
California State Law requires that all contractors be licensed by the California Contractors State License Board (CSLB).
Various classifications. HVAC is C-20 "Warm Air Heating, Ventilating, and Air Conditioning". There are over 12,000 licensed HVAC contractors in CA.
CSLB has enforcement authority.
  CSLB has a Statewide Investigative Fraud Team (SWIFT)
  Cities separately enforce – like San Francisco
Consumers can easily check if a contractor is licensed or not.
  https://www2.cslb.ca.gov/OnlineServices/CheckLicenseII/CheckLicense.aspx
Consumers can easily file complaints.
  https://www.cslb.ca.gov/Consumers/Filing_a_Complaint/
Many cities actively promote use of, and checking for, licensed contractors.
  https://www.riverbank.org/182/Building
  https://www.ci.patterson.ca.us/140/Building-Division
  https://www.lacityattorney.org/unlicensed-contractor-fraud **PUBLIC CAMPAIGN**

## Slide 44: Technician Training
Training Programs are available or in progress
•ACCA found at: https://www.acca.org/certification
•NATE found at: https://www.natex.org/site/1/Home
•RSES found at: https://www.rses.org/hydrocarbons.aspxhttps://www.rses.org/hydrocarbons.aspxhttps://www.rses.org/hydrocarbons.aspx
•OEMs will have training and/or detailed service manuals in order for products to be listed (UL 60335-2-40 Annex DD)
•The refrigeration market has already transitioned to A3s (vending machines, refrigerators)
  IHACI Training (California contractor association):
http://www.ihaci.org/education-training/
http://www.ihaci.org/education-training/class-description/

## Slide 45: Sensor Mitigation Strategy: Prevent Ignition
  Internal sensors detect refrigerant inside equipment before an external leak occurs.
  UL 60335-2-40 requires an internal sensors and controls to mitigate leak if the charge is above m1 where the greatest concentration will be so that it is detected.

## Slide 46: Sensor Life
•What happens if expected sensor life is shorter than expected product life?
•UL 60335-2-40 addresses this situation.
•Sensors are either “refrigerant sensor” or “limited life refrigerant sensor.”
•Annex LL .8 addresses this situation by mandating that if a sensor would need to be replaced, it must take by going into continuous circulation mode at a minimum airflow.
Lifetime depends on which product the manufacturer selects. Many have reported that sensors can outlast equipment.
Similar to smoke detectors, self-test is required to detect failure just in case there is a premature failure
The same requirement applies for failure of self-check.

## Slide 47: Leak Sensing and Mitigation Operation
The approach used by Safety Standards for the application of A2L refrigerants is to sense the leaking refrigerant inside the unit and automatically mitigate using circulated airflow before the refrigerant reaches 25% of LFL in the occupied space outside the unit.
  Refrigerant sensors/detectors are required to factory installed in the unit and qualified and certified for settings and accuracy as well as location
  When the sensor/detector detects a refrigerant leak, inside the units the indoor fan is turned on to circulate airflow and dilute the refrigerant. The fan continues to run until the detector resets plus and additional 5 mins.
  Alternate approach is continuous fan operation, but that increases energy use
Annex MM of UL60335-2-40 has defined requirements for qualification of the sensor/detector location
Sensor Location

## Slide 48: UL60335-2-40 Sensor Location Requirements
As per annex MM 2.6
The measured concentration of refrigerant gas at the location of the REFRIGERANT DETECTION
SYSTEM sensor shall exceed the set point of the detection system used within 90 s from the start of the release. Where multiple sensors are applied with the REFRIGERANT DETECTION SYSTEM, if the concentration at any single sensor location exceeds the set point of the detection system used within 90 s from the start of the release, the REFRIGERANT DETECTION SYSTEM sensor location shall be considered in compliance.
The purpose of this test is to determine if the selected location of the sensor is in a good place to detect a leak inside the unit and acceptable to detect a leak.

## Slide 49: Leak Sensing and Mitigation Operation
The figures show the results of the CFD and testing at the entrance to the short return duct (location 5)
5
Time ( sec )
R454B v/v%
1.5 g/s
0.68 g/s
0.38 g/s
Leak Rate
CFD Results (1.5 g/s)
R454B v/v%
LFL
25%
LFL
1
Leak and Sensor location

## Slide 50: Fluorocarbon combustion products
Hydrogen fluoride (HF) is a combustion product of old A1 refrigerants (in use for 90 years) and new A2L refrigerants
  HF forms when any fluorocarbon refrigerant, including those used today, undergoes combustion, partial combustion, or thermal decomposition
  HF gas is a lung irritant and HF acid, depending on concentration, is a skin irritant
Hydrogen Iodide (HI) and HFC-23 are additional combustion products R-466A
  R-466A contains CF3I
  HI gas is a lung irritant and HI acid, depending on concentration, is a skin irritant

## Slide 51: Wild Fire Concerns
A2L Residential AC system
Less than 4 gallons of an A2L refrigerant
Difficult to ignite (High MIE)
Low heat of combustion
propane
120 gallon tank of propane allowed 10 feet from house.
Low minimum ignition energy (MIE)
Higher heat of combustion

## Slide 52: Did you know?
Olive oil, a Class IIIB combustible liquid has a heat of combustion of over 17,000 Btu/lb. Difluoromethane (R-32), a Category 2 flammable gas, has a heat of combustion of 4,041 Btu/lb or one fourth that of olive oil.

## Slide 53
(Source: NFPA 58. Appendix I)

## Slide 54: Wild Fire
Concerns have been raised about the increase risk to a structure exposed to a wild fire
At the temperatures of a fire 600 C to 1,100 C the A2L and A1 refrigerants will be flammable as well as the oil in HVAC systems
If a leak occurs near an active fire are there additional risk with A2L refrigerants
The heat of combustion for typical A1 and A2L refrigerants are;
  Nominal A2L refrigerant Heat of Combustion = 4,400 BTU/lb.
  R-410A refrigerant Heat of Combustion = 2,800 BTU/lb.
In a fire 100% combustion typically does not occur but if we assume 100% combustion and a charge of 15 lbs. the difference in fuel value is;
  (4,400 – 2,800) x 15 = 24,000 BTU
This difference (A2L vs A1) is equivalent to additional fuel value of:
  3.4 lbs. dry wood (~30% of an 8 ft. length of kiln-dried 2x4)
  1.7 lbs. Duraflame™ wax fire log (~38% of a single fire log)
There is negligible added fuel value in this scenario due to A2L refrigerant usage

## Slide 55: What about a leak in an outdoor condensing unit during a wildfire?
The evaluate this we are doing CFD studies of various leak scenarios for an outside condensing unit
The following are the results for a ¼ hole in a condenser tube angled up at 45 degrees which results in a full loss of charge in 1 minute. There is no wind and the unit is in a corner of a building structure
Leak rate include pressure degradation
¼ hole results in full charge loss in 1 minute
As you can see at this very high leak rate the flammable mass region is very small
Leak Location

## Slide 56: What is different in a house fire? (HVAC unit not involved)
Scenarios:
First responder enters house during fire, HVAC line is leaking onto hot surface (no fire at leak site)
First responder enters house after fire, HVAC line is leaking onto hot surface (no fire at leak site)

## Slide 57: What is different in a house fire? (HVAC unit not on fire)
Scenarios
First responder severs line during house fire
Equipment line breaks due to line failure while first responder is nearby

## Slide 58: Potential Refrigerant Fuel Load
Worst case scenario = externally fueled fire, complete charge loss (typical residential ducted split unit charge ~ 15 lbs.)
  Nominal A2L refrigerant Heat of Combustion = 4,400 BTU/lb.
  R-410A refrigerant Heat of Combustion = 2,800 BTU/lb.
Assuming all refrigerant leaked and burned, fuel value difference between the A2L and R-410A would be:
  (4,400 – 2,800) x 15 = 24,000 BTU
This difference (A2L vs A1) is equivalent to additional fuel value of:
  3.4 lbs. dry wood (~30% of an 8 ft. length of kiln-dried 2x4)
  1.7 lbs. Duraflame™ wax fire log (~38% of a single fire log)
There is negligible added fuel value in this scenario due to A2L refrigerant usage

## Slide 59: What is different? Wildfire with 410A, A2L or a Propane tank?
Propane Tank Fire
Image from report - - - > https://virginiabeach.legalexaminer.com/legal/defective-dangerous-products/injuries-caused-by-propane/
https://www.kcrg.com/content/news/Central-City-house-fire-re-routing-traffic-493532011.html
120 Gallon Vertical Propane Tank – ASME
https://www.kleen-ritecorp.com/p-37891-120-gallon-vertical-propane-tank-asme.aspx
Charge is unlikely to exceed 35 lbs. A2L in a single residential split system.
120 gallon propane tank contains up to 60 lbs.
Propane Tank Fire

## Slide 60: What is different in a wildfire igniting a 410A unit vs HC tank?
Scenarios
First responder comes to house and HVAC unit is on fire and proceeds to put out HVAC unit
First responder comes to house and Propane tank is on fire and first responder takes appropriate action (?)

## Slide 61: Damage to Refrigerant Lines During a Fire
There has been concerns expressed about damage to refrigerant lines inside a wall during fire fighting
UL demonstration project will show impact of a leak
To determine the potential for line damage we have done some experiments on damage to a line from an ax where we evaluated a ¼ copper line and a ½ copper line
With a direct hit from an ax the lines were damaged but a leak did not occur.
For the ¼ inch line with a little post stressing the line did break but the resulting hole size was only 0.002 x .30 slot which at 500 F temperatures for R-32 would result in a 0.049 lb/min leak rate
½ inch line (no leak)
¼ inch line (no leak)
¼ line with post stressing
0.002 x .30 slot

## Slide 62: What if there is a catastrophic leak and there is a power outage and there is an external fire?
Non-causative, multiple failures that each have low probability of occurring
No power  no ignition source within unit
+ Catastropic leak must be sufficient to reach LFL (10x higher than propane)
+ External fire
Bottom line: Less than 4 gallons of A2L refrigerant is present which is difficult to ignite and has low heat of combustion

## Slide 63: Water Heater in a Closet
This has been considered in UL60335-2-40 with requirements on the joints at the fan coil
  Joints either must be ISO 14903 qualified or inside the fan coil
This also has been addressed in standard for water heaters which require flame arrestors after 2004 to protect against exposure to flammable gas mixtures in a garage
So the potential for a leak in the closet has been address but testing has been done in the industry to evaluate if a leak did occur
Shown is a test setup where a water heater and a fan coil were installed in a small closet and a leak was introduced that resulted in a flammable concentration around the water heat with a standing pilot. The flame arrestor was removed for this testing
Tests were run with R-32 (A2L), R-1234ze(E) and R-410A (A1) and no external combustion was seen and only extension of the pilot flame occurred
R-410A
(A1)
R-1234ze(E) A2L
R--32 A2L

## Slide 64: Seismic: AC units are highly qualified for vibration
AC units highly qualified for vibration
  Shipping vibration
  Steady State operational vibration
  VRF has additional requirements in UL/CSA 60335-2-40 for vibration
Piping
Copper tubing is robust in vibration.
    Expansion loops
    Not rigidly mounted
    Seismic isolators are required in California Building Code
What are the requirements today?
Only Category 4 (e.g. hospitals, disaster relief) Certificate of seismic code compliance
There are no seismic requirements for boilers in residential
Water heaters must be secured in residential setting

## Slide 65: Question - Seismic
This is not a new concern and is covered in the existing IBC commercial code in section 1705.2 and 1705.2 and in the Residential in Chapter 4, 6, 10
The requirements for construction of the building depend on the Seismic Design Categories of C, Do, D1, and D2 for residential building in section R301.2.2 of the 2019 California Residential code.
  In active zones, additional requirements are required for walls, floors
  We did not see specific requirements for HVAC systems.
For commercial buildings the IBC code refer to the ASCE-7 standard and California OSHPD who interprets the requirements for California
  For critical buildings like public assembly there are certification requirements that include verification of durability and operability in a seismic event
  ASCE-7 allow for qualification one of the following three method which will continue to be used as required;
    Calculations
    Shaker Table Testing for transport testing completed in y and z
    Historical
The UL60335-2-40 and ASHRAE 15 standard do not address seismic qualification, but do require vibration, shipping testing as well as most manufactures internal qualification testing
The new A2L systems do have more robust requirements for piping and joints and field testing of piping and are likely more durable than current A1 based refrigerants units.

## Slide 66: Shaker Table Testing
Shaker Table testing for transport is in y and z direction
Higher frequency
Longer test (hours)
Seismic test is low frequency, high displacement test in y direction only

## Slide 67: AHRI Research to Verify IEC 60335-2-40
US TAG wanted to verify the IEC 60335-2-40 --> $7 million by AHRI and ASHRAE
  US AC industry is more conservative
  Different built environment in US
  Individual companies and international research also invested in testing
  Research completed to inform the safety standards
  AHRI created videos of some of the research related to A2L and A3 refrigerants.
  Still photos of the videos can be found in the final reports on the AHRTI website
8 hours to walk through research to provide context .
  AHRI willing to start this process now through a virtual forum
  When pandemic conditions allow for an in-person, we can complete the process.
AHRI has presented videos jointly with UL in Northbrook Illinois
  Oct 2018: Invitations sent to fire service with more than 100 attendees for 2-day session on research for both air conditioning and commercial refrigeration -
  Jan 2020: Private session on air conditioning research inviting only specific members of fire service as directed by and including Jim Dominik

## Slide 68: Wildfire Concerns
A2L Residential AC system
Less than 4 gallons of an A2L refrigerant
Difficult to ignite (High MIE)
Low heat of combustion
propane
120 gallon tank of propane allowed 10 feet from house.
Low minimum ignition energy (MIE)
Higher heat of combustion

## Slide 70
DISCLAIMER: The information contained in the conference presentations are intended primarily to inform industry experts and code committees revising relevant national and regional safety codes. Please confine the sharing of this information to within your company. AHRI makes no claims, promises, or guarantees about the accuracy, completeness, or adequacy of the contents of the information, and expressly disclaims liability for errors and omissions in the content of the information.